## Dev1
SignalFire Ranger Tag Guide: Firmware Revision v0.1.15 - Subject to change in future firmware revisions - Tags colored orange or blue depend on Feature Flags being enabled or disabled.
Tag Name | Alias | DataType | Writable | Part of periodic report | Report on change | Units | Low Range | High Range | Default | Description
bdSeq | 0 | UINT32 | No | No | No |  |  |  |  | Implemented as per SparkPlug specification. Counts the number of MQTT connections over the life of the device.
Node Control/Reboot | 1 | BOOLEAN | Yes | No | No |  |  |  |  | Writing any value to this tag will cause the Ranger node to reboot.
Node Control/Rebirth | 2 | BOOLEAN | Yes | No | No |  |  |  |  | Writing any value to this tag will cause the Ranger node to resend SparkPlug BIRTH information. (NOTE: Does not disconnect from MQTT broker.)
Node Control/Next Server | 3 | BOOLEAN | Yes | No | No |  |  |  |  | Writing any value to this tag will cause the Ranger node to temporarily disconnect from the MQTT broker. The node will immediately try to reconnect.
Node Control/Group ID | 4 | STRING | Yes | No | No |  |  |  | none | Writing to this changes the group_id within the SparkPlug MQTT topic namespace the Ranger will use to communicate. See section 6.1 "Sparkplug Topic Namespace Elements" of the SparkPlug spec for more details
Properties/HW Rev | 5 | STRING | No | No | No |  |  |  |  | Reports a string identifying the make and model of hardware. Will be "SignalFire Ranger (v1)" for all current Ranger models.
Properties/HW Config | 6 | STRING | No | No | No |  |  |  | DCDC | Reports a string which identifies factory hardware configuration of the node. "DCDC" indicates 13/18V AIN sensor power. "DCDC-A2" indicates 13/18V AIN sensor power, and A2D1 sensor daughtercard.
Properties/SW Rev | 7 | STRING | Yes | No | No |  |  |  |  | Reports a string identifying the firmware version running on the Ranger. FOTA updates can be triggered by writing special names provided by SignalFire support to this tag.
Properties/Name | 8 | STRING | Yes | No | Yes |  |  |  |  | Reports a customizable name for this Ranger node. This is purely informational and can be modified at will by the customer by writing to the tag.
Properties/Report Interval | 9 | UINT32 | Yes | No | Yes | s | 5 | 43200 | 300 | The interval between periodic reports. Writing any value to this tag configures the interval and also triggers an immediate sensor check and report. Rewriting the current value is the recommended method to trigger an immediate periodic report.
Console | 10 | STRING | Yes | No | No |  |  |  |  | Used for remote debug/support of the Ranger node.
Temperature | 11 | FLOAT | No | Yes | No | °C | -40 | 125 |  | Reports the current electronics temperature of the cellular modem
Battery | 12 | FLOAT | No | Yes | No | V | 0 | 5 |  | Reports the voltage of the battery, sampled during reports while sensor is powered on.
Connect Time | 13 | DATETIME | No | No | No |  |  |  |  | Timestamp of when the Ranger most recently connected to the MQTT broker, given as milliseconds since January 1, 1970 UTC
Local UTC Offset | 14 | INT16 | No | No | No | minutes | -720 | 840 |  | Local timezone offset from UTC at the Ranger's location, as reported to it by the cellular towers
Feature Flags | 15 | UINT32 | Yes | No | Yes |  | 0 | 3 | 0 | Optional Features Enabled Flags: bit0: Enable/Disable DIN1 Flow Measurement, bit1: Enable/Disable DIN2 Flow Measurement, bit2: Enable/Disable AIN1 Flow Measurement. Changing feature flags causes a disconnect and reconnect to the MQTT broker to add/remove tags.
GNSS/Active | 16 | BOOLEAN | Yes | No | Yes |  |  |  |  | Reports if the GNSS subsystem is currently active and trying to get a fix. Writing 1 or 0 to this tag will immediately enable or disable the GNSS receiver.
GNSS/Interval | 17 | UINT32 | Yes | No | Yes | s | 0 | 64800 | 0 | Controls the amount of time between automatic GNSS location fixes. Setting this to 0 disables automatic fixes.
GNSS/Timeout | 18 | UINT32 | Yes | No | Yes | s | 0 | 600 | 300 | Controls the amount of time the Ranger will try to get a GNSS fix before giving up.
GNSS/NMEA | 19 | STRING | No | No | Yes |  |  |  |  | NMEA string(s) from the most recent GNSS fix. This tag will have a timestamp included in the SparkPlug payload metadata indicating when the fix was acquired if it was not within the past minute.
Modem/Rev | 20 | STRING | No | No | No |  |  |  |  | Reports a string identifying the firmware version running on the cellular modem.
Modem/Console | 21 | STRING | Yes | No | No |  |  |  |  | Used for remote debug/support of the Ranger node.
Modem/Connect Delay | 22 | UINT32 | No | No | No | ms |  |  |  | Reports how many milliseconds the cellular modem took to fully register with a cell tower for the most recent offline-to-online transition
Modem/RSRP | 23 | INT16 | No | Yes | No | dBm | -140 | -44 |  | Reports strength of the cellular signal as received by the modem
Modem/Roaming | 24 | BOOLEAN | No | No | Yes |  |  |  |  | Reports if the cellular service in use is considered "roaming" by the SIM card.
Modem/CEREG/CI | 25 | STRING | No | No | Yes |  |  |  |  | Reposts the E-UTRAN cell ID of the current cellular service in use.
Modem/CEREG/TAC | 26 | STRING | No | No | Yes |  |  |  |  | Reports the Tracking Area Code (TAC) of the current cellular service in use.
Modem/CEREG/ACT | 27 | UINT8 | No | No | Yes |  |  |  |  | Reports the activation type of the current cellular service in use. (7=LTE-M1, 9=NB-IOT)
Modem/Operator | 28 | STRING | No | No | Yes |  |  |  |  | Reports the name of the current cellular operator in use, as reported by the cellular tower
Modem/MCCMNC | 29 | STRING | No | No | Yes |  |  |  |  | Reports the mobile country code and mobile network code (MCCMNC) of the current cellular service in use
Dev1/Report Count | 30 | UINT32 | No | Yes | No |  |  |  |  | Counts the number of periodic reports that have been generated. Is useful for examining report history and determining when reports were generated and where data might be missing.
Dev1/DIN1 | 31 | BOOLEAN | No | Yes | Configurable |  |  |  |  | Reports the current state of the DIN1 input. Will be 0 for OPEN and 1 for CLOSED. Optionally reported immediately on every change.
Dev1/DIN1 Count | 32 | UINT64 | Yes | Yes | Configurable | cycles |  |  |  | Reports how many times DIN1 has cycled. Increments by 1 for every OPEN-to-CLOSE transition of DIN1. Writing to this tag from SparkPlug will adjust the current count to the given value.
Dev1/DIN1 Average Frequency | 33 | FLOAT | No | Yes | No | Hz |  |  |  | Reports the average frequency of DIN1, calculated between the prior and current periodic reports.
Dev1/DIN1 Instantaneous Frequency | 34 | FLOAT | No | Yes | No | Hz |  |  |  | Reports the instantaneous frequency of DIN1, sampled with a 2 second gate time.
Dev1/DIN1 Config/Report on Change | 35 | BOOLEAN | Yes | No | Yes |  |  |  | FALSE | Controls whether a report is immediately generated on any change of DIN1. Any immediate report will only include DIN1 values, and not a full periodic report. 1 = Report on change
Dev1/DIN1 Config/Debounce Delay | 36 | UINT32 | Yes | No | Yes | ms | 0 | 5000 | 0 | Configures a debounce delay on the DIN1 input. The debounce timer is disabled when set to 0.
Dev1/DIN1 Flow Total | 37 | FLOAT | Yes | Yes | No | Configurable |  |  |  | Reports the flow total of DIN1, calculated using KFactor, and converted from KFactor Units to Volume Units. Flow Total is preserved when KFactor or KFactor Units change. Writing to this tag from SparkPlug will adjust the current flow total to the given value and reset the flow for both this period and last period.
Dev1/DIN1 Flow This Period | 38 | FLOAT | Yes | Yes | Yes | Configurable |  |  |  | Reports the flow this period of DIN1, calculated using KFactor, and converted from KFactor Units to Volume Units. Flow This Period is preserved when KFactor or KFactor Units change. Writing 0 to this tag from SparkPlug will reset the value.
Dev1/DIN1 Flow Last Period | 39 | FLOAT | Yes | Yes | Yes | Configurable |  |  |  | Reports the flow last period of DIN1, calculated using KFactor, and converted from KFactor Units to Volume Units. Flow Last Period is preserved when KFactor or KFactor Units change. Writing 0 to this tag from SparkPlug will reset the value.
Dev1/DIN1 Instantaneous Flow Rate | 40 | FLOAT | No | Yes | No | Configurable |  |  |  | Reports the average flow rate of DIN1, calculated between the prior and current periodic reports.
Dev1/DIN1 Average Flow Rate | 41 | FLOAT | No | Yes | No | Configurable |  |  |  | Reports the instantaneous flow rate of DIN1, sampled with a 2 second gate time.
Dev1/DIN1 Config/KFactor | 42 | FLOAT | Yes | No | Yes |  | 0 < |  | 1 | The KFactor to use to calculate DIN1 Flow. This is the number of DIN1 pulses per DIN1 KFactor Unit of volume.
Dev1/DIN1 Config/KFactor Units | 43 | STRING | Yes | No | Yes |  |  |  | gal | The units of volume of the DIN1 KFactor. (gal, bbl, cm3, L, m3, ft3, Mgal, imp gal, imp Mgal, ML, ac·in, ac·ft)
Dev1/DIN1 Config/Volume Units | 44 | STRING | Yes | No | Yes |  |  |  | gal | The volume units to use for calculating DIN1 Flow Total. (gal, bbl, cm3, L, m3, ft3, Mgal, imp gal, imp Mgal, ML, ac·in, ac·ft)
Dev1/DIN1 Config/Timebase | 45 | STRING | Yes | No | Yes |  |  |  | sec | The timebase to use for calculating DIN1 Flow Rates. (sec, min, hour, day)
Dev1/DIN1 Config/Flowrate Units | 46 | STRING | Yes | No | Yes |  |  |  | gal | The volume units to use for calculating DIN1 Flow Rates. (gal, bbl, cm3, L, m3, ft3, Mgal, imp gal, imp Mgal, ML, ac·in, ac·ft)
Dev1/DIN2 | 47 | BOOLEAN | No | Yes | Configurable |  |  |  |  | Reports the current state of the DIN2 input. Will be 0 for OPEN and 1 for CLOSED. Optionally reported immediately on every change.
Dev1/DIN2 Count | 48 | UINT64 | Yes | Yes | Configurable | cycles |  |  |  | Reports how many times DIN2 has cycled. Increments by 1 for every OPEN-to-CLOSE transition of DIN2. Writing to this tag from SparkPlug will adjust the current count to the given value. Optionally reported immediately on every change.
Dev1/DIN2 Average Frequency | 49 | FLOAT | No | Yes | No | Hz |  |  |  | Reports the average frequency of DIN2, calculated between the prior and current periodic reports.
Dev1/DIN2 Instantaneous Frequency | 50 | FLOAT | No | Yes | No | Hz |  |  |  | Reports the instantaneous frequency of DIN2, sampled with a 2 second gate time.
Dev1/DIN2 Config/Report on Change | 51 | BOOLEAN | Yes | No | Yes |  |  |  | FALSE | Controls whether a report is immediately generated on any change of DIN2. Any immediate report will only include DIN2 values, and not a full periodic report. 1 = Report on change
Dev1/DIN2 Config/Debounce Delay | 52 | UINT32 | Yes | No | Yes | ms | 0 | 5000 | 0 | Configures a debounce delay on the DIN2 input. The debounce timer is disabled when set to 0.
Dev1/DIN2 Flow Total | 53 | FLOAT | Yes | Yes | No | Configurable |  |  |  | Reports the flow total of DIN2, calculated using KFactor, and converted from KFactor Units to Volume Units. Flow Total is preserved when KFactor or KFactor Units change. Writing to this tag from SparkPlug will adjust the current flow total to the given value and reset the flow for both this period and last period.
Dev1/DIN2 Flow This Period | 54 | FLOAT | Yes | Yes | Yes | Configurable |  |  |  | Reports the flow this period of DIN2, calculated using KFactor, and converted from KFactor Units to Volume Units. Flow This Period is preserved when KFactor or KFactor Units change. Writing 0 to this tag from SparkPlug will reset the value.
Dev1/DIN2 Flow Last Period | 55 | FLOAT | Yes | Yes | Yes | Configurable |  |  |  | Reports the flow last period of DIN2, calculated using KFactor, and converted from KFactor Units to Volume Units. Flow Last Period is preserved when KFactor or KFactor Units change. Writing 0 to this tag from SparkPlug will reset the value.
Dev1/DIN2 Instantaneous Flow Rate | 56 | FLOAT | No | Yes | No | Configurable |  |  |  | Reports the instantaneous flow rate of DIN2, sampled with a 2 second gate time.
Dev1/DIN2 Average Flow Rate | 57 | FLOAT | No | Yes | No | Configurable |  |  |  | Reports the average flow rate of DIN2, calculated between the prior and current periodic reports.
Dev1/DIN2 Config/KFactor | 58 | FLOAT | Yes | No | Yes |  | 0 < |  | 1 | The KFactor to use to calculate DIN2 Flow. This is the number of DIN2 pulses per DIN2 KFactor Unit of volume.
Dev1/DIN2 Config/KFactor Units | 59 | STRING | Yes | No | Yes |  |  |  | gal | The units of volume of the DIN2 KFactor. (gal, bbl, cm3, L, m3, ft3, Mgal, imp gal, imp Mgal, ML, ac·in, ac·ft)
Dev1/DIN2 Config/Volume Units | 60 | STRING | Yes | No | Yes |  |  |  | gal | The volume units to use for calculating DIN2 Flow Total. (gal, bbl, cm3, L, m3, ft3, Mgal, imp gal, imp Mgal, ML, ac·in, ac·ft)
Dev1/DIN2 Config/Timebase | 61 | STRING | Yes | No | Yes |  |  |  | sec | The timebase to use for calculating DIN2 Flow Rates. (sec, min, hour, day)
Dev1/DIN2 Config/Flowrate Units | 62 | STRING | Yes | No | Yes |  |  |  | gal | The volume units to use for calculating DIN2 Flow Rates. (gal, bbl, cm3, L, m3, ft3, Mgal, imp gal, imp Mgal, ML, ac·in, ac·ft)
Dev1/DOUT1 | 63 | BOOLEAN | Yes | Yes | Yes |  |  |  |  | Reports the current state of the DOUT1 relay. Writing to this tag will control the relay. The Ranger will confirm the change by reporting this tag back immediately with the new state.
Dev1/DOUT1 Config/Failsafe Timer | 64 | UINT32 | Yes | No | Yes | s | 0 | 3600 | 0 | Configures a failsafe timer for the DOUT1 relay. If the Ranger is not fully connected to its configured Cloud Service for this period of time, the DOUT1 relay will be automatically de-energized. 0 = Disabled
Dev1/AIN1 | 65 | FLOAT | Yes | Yes | No | Configurable |  |  |  | Reports the current reading of the AIN1 terminal, scaled between Scale Low and Scale High. If scaling has not been configured, this will be the same units, range, and value as the "AIN1 Raw" tag. Writing to this tag zeroes AIN1 to the value written.
Dev1/AIN1 Raw | 66 | FLOAT | No | Yes | No | Configurable |  |  |  | Reports the current reading of the AIN1 terminal. This value is before the scaling, and will be reported as a value in either the 4-20mA, 1-5V, or 0-15V range, depending on the position of the Analog IN Select switch on the Ranger.
Dev1/AIN1 Config/Scale Low | 67 | FLOAT | Yes | No | Yes |  |  |  | 0 | The lower range value to use when scaling AIN1.
Dev1/AIN1 Config/Scale High | 68 | FLOAT | Yes | No | Yes |  |  |  | 0 | The upper range value to use when scaling AIN1.
Dev1/AIN1 Config/Scale Adjust | 69 | FLOAT | Yes | No | Yes |  |  |  | 0 | The +/- adjustment to use when scaling AIN1.
Dev1/AIN1 Config/Scale Units | 70 | STRING | Yes | No | Yes |  |  |  |  | The AIN1 scaled units description
Dev1/AIN1 Config/Sensor On Time | 71 | FLOAT | Yes | No | Yes | s | -1 | 120 | 2 | The time duration to enable sensor power before reading AIN sensors on each periodic report. A value of 0 disables sensor power. A value of -1 keeps sensor power enabled continuously.
Dev1/AIN1 Config/Sensor Voltage | 72 | UINT32 | Yes | No | Yes | V |  |  | 13 | The voltage to use to power AIN sensors. Writable to 13 or 18 Volts
Dev1/AIN1 Config/Sampling Interval | 73 | FLOAT | Yes | No | Yes | s | 0 | 60 | 0 | The interval between AIN sensor readings. (Not Yet Implemented)
Dev1/AIN1 Config/Specific Gravity | 74 | FLOAT | Yes | No | Yes |  |  |  | 1 | The specific gravity to divide the AIN1 reading by, in applications reading liquid level from a pressure sensor.
Dev1/AIN1 Config/Low Threshold | 75 | FLOAT | Yes | No | Yes | Configurable |  |  | 0 | The low threshold for alarming on AIN1.
Dev1/AIN1 Config/High Threshold | 76 | FLOAT | Yes | No | Yes | Configurable |  |  | 0 | The high threshold for alarming on AIN1.
Dev1/AIN1 Config/Zero Offset | 77 | FLOAT | Yes | No | Yes | Configurable |  |  | 0 | The calibrated zero offset for AIN1. Writing 0 to this tag clears the zero offset for AIN1.
Dev1/AIN1 Flow Total | 78 | FLOAT | Yes | Yes | No | ac·ft |  |  |  | Reports the flow total of AIN1, calculated by scaling AIN1 to ft3/sec and integrating over the time between AIN1 samples. Writing to this tag from SparkPlug will adjust the current flow total to the given value and reset the flow for both this period and last period.
Dev1/AIN1 Flow This Period | 79 | FLOAT | Yes | Yes | Yes | ac·ft |  |  |  | Reports the flow this period of AIN1, calculated by scaling AIN1 to ft3/sec and integrating over the time between AIN1 samples. Writing 0 to this tag from SparkPlug will reset the value.
Dev1/AIN1 Flow Last Period | 80 | FLOAT | Yes | Yes | Yes | ac·ft |  |  |  | Reports the flow last period of AIN1, calculated by scaling AIN1 to ft3/sec and integrating over the time between AIN1 samples. Writing 0 to this tag from SparkPlug will reset the value.
Dev1/AIN1 Config/Volume Units | 81 | STRING | Yes | No | Yes |  |  |  | ac·ft | The volume units to use for calculating AIN1 Flow Total. (ac·ft)
Dev1/Sensor Power Override | 82 | UINT32 | Yes | No | Yes | s | 0 | 3600 | 0 | Manually override AIN sensor power on for up to 3600 seconds. Writing a value of 1 - 3600 seconds will turn on AIN sensor power for that many seconds. Writing a value of 0 disables the override, allowing AIN sensor power to turn off.
Dev1/Fast Reporting/Active | 83 | BOOLEAN | No | No | Yes |  |  |  |  | Reports if Fast Reporting Mode is currently active.
Dev1/Fast Reporting/Enabled | 84 | BOOLEAN | Yes | No | Yes |  |  |  | FALSE | Controls whether Fast Reporting Mode is enabled or disabled. Disabling Fast Reporting Mode while it is active will immediately end Fast Reporting.
Dev1/Fast Reporting/Report Interval | 85 | UINT32 | Yes | No | Yes | s | 5 | 43200 | Properties/Report Interval | The Report Interval to use in Fast Reporting Mode. See the "Properties/Report Interval" tag.
Dev1/Fast Reporting/Sensor On Time | 86 | FLOAT | Yes | No | Yes | s | -1 | 120 | Dev1/AIN1 Config/Sensor On Time | The Sensor On Time to use in Fast Reporting Mode. See the "Dev1/AIN1 Config/Sensor On Time" tag.
Dev1/Fast Reporting/Mode | 87 | STRING | Yes | No | Yes |  |  |  | Until Cleared | The Fast Reporting Mode control logic for stay in Fast Reporting Mode once it is active. Options are "Until Cleared" or "Duration"
Dev1/Fast Reporting/Duration | 88 | UINT32 | Yes | No | Yes | s | 5 | 43200 | 3600 | The duration to stay in Fast Reporting Mode once triggered, if the Fast Report Mode is set to "Duration"
Dev1/Fast Reporting/Condition | 89 | STRING | Yes | No | Yes |  |  |  | Any | The Fast Reporting condition to use when evaluating the Fast Report Triggers. Options are "Any" or "All" triggers evaluating TRUE to enter Fast Reporting Mode.
Dev1/Fast Reporting/Triggers | 90 | STRING | Yes | No | Yes |  |  |  |  | Defines the Fast Reporting Triggers, in CSV format. Up to 4 Fast Reporting Triggers can be defined.
Dev1/Relay Control/Enabled | 91 | BOOLEAN | Yes | No | Yes |  |  |  | FALSE | Controls whether the Relay Control is enabled or disabled (i.e., whether the Relay Control Triggers will be evaluated and applied). When enabled, a write to the Dev1/DOUT1 tag will be ignored.
Dev1/Relay Control/Failsafe | 92 | BOOLEAN | Yes | No | Yes |  |  |  | FALSE | Controls whether missing source data sets trigger condition to de-energize.
Dev1/Relay Control/MinEnergize | 93 | UINT32 | Yes | No | Yes | s | 1 | 43200 | 1 | The minimum time the relay must be energized once triggered.
Dev1/Relay Control/Condition | 94 | STRING | Yes | No | Yes |  |  |  | Any | The Relay Control condition to use when evaluating the Relay Control Triggers. Options are "Any" or "All" triggers evaluating TRUE to energize relay.
Dev1/Relay Control/Triggers | 95 | STRING | Yes | No | Yes |  |  |  |  | Defines the Relay Control Triggers, in CSV format. Up to 8 Relay Control Triggers can be defined.
Dev1/Contract Period/Mode | 96 | UINT8 | Yes | No | Yes |  |  |  | Daily | The time period in which to change the periodic flow totals. Options are "Daily" or "Hourly".
Dev1/Contract Period/Hour | 97 | UINT8 | Yes | No | Yes | hours | 0 | 23 | 0 | The hour that the contract period will change. (Available oonly in "Daily" mode.)
Dev1/Contract Period/Minute | 98 | UINT8 | Yes | No | Yes | minutes | 0 | 59 | 0 | The minute that the contract period will change.

## DevA2
SignalFire Ranger Tag Guide: Firmware Revision v0.1.15 - Subject to change in future firmware revisions - Tags colored orange or blue depend on Feature Flags being enabled or disabled.
Tag Name | Alias | DataType | Writable | Part of periodic report | Report on change | Units | Low Range | High Range | Default | Description
Feature Flags | 99 | UINT32 | Yes | No | Yes |  | 0 | 1 | 0 | Optional Features Enabled Flags: bit0: Enable/Disable DIN3 Flow Measurement, bit1: Enable/Disable AIN2 Flow Measurement, bit2: Enable/Disable AIN3 Flow Measurement. Changing feature flags causes a disconnect and reconnect to the MQTT broker to add/remove tags.
DIN3 | 100 | BOOLEAN | No | Yes | Configurable |  |  |  |  | Reports the current state of the DIN3 input. Will be 0 for OPEN and 1 for CLOSED. Optionally reported immediately on every change.
DIN3 Count | 101 | UINT64 | Yes | Yes | Configurable | cycles |  |  |  | Reports how many times DIN3 has cycled. Increments by 1 for every OPEN-to-CLOSE transition of DIN3. Writing to this tag from SparkPlug will adjust the current count to the given value.
DIN3 Average Frequency | 102 | FLOAT | No | Yes | No | Hz |  |  |  | Reports the average frequency of DIN3, calculated between the prior and current periodic reports.
DIN3 Instantaneous Frequency | 103 | FLOAT | No | Yes | No | Hz |  |  |  | Reports the instantaneous frequency of DIN3, sampled with a 2 second gate time.
DIN3 Config/Report on Change | 104 | BOOLEAN | Yes | No | Yes |  |  |  | FALSE | Controls whether a report is immediately generated on any change of DIN3. Any immediate report will only include DIN3 values, and not a full periodic report. 1 = Report on change
DIN3 Config/Debounce Delay | 105 | UINT32 | Yes | No | Yes | ms | 0 | 5000 | 0 | Configures a debounce delay on the DIN3 input. The debounce timer is disabled when set to 0.
DIN3 Flow Total | 106 | FLOAT | Yes | Yes | No | Configurable |  |  |  | Reports the flow total of DIN3, calculated using KFactor, and converted from KFactor Units to Volume Units. Flow Total is preserved when KFactor or KFactor Units change. Writing to this tag from SparkPlug will adjust the current flow total to the given value and reset the flow for both this period and last period.
DIN3 Flow This Period | 107 | FLOAT | Yes | Yes | Yes | Configurable |  |  |  | Reports the flow this period of DIN3, calculated using KFactor, and converted from KFactor Units to Volume Units. Flow This Period is preserved when KFactor or KFactor Units change. Writing 0 to this tag from SparkPlug will reset the value.
DIN3 Flow Last Period | 108 | FLOAT | Yes | Yes | Yes | Configurable |  |  |  | Reports the flow last period of DIN3, calculated using KFactor, and converted from KFactor Units to Volume Units. Flow Last Period is preserved when KFactor or KFactor Units change. Writing 0 to this tag from SparkPlug will reset the value.
DIN3 Instantaneous Flow Rate | 109 | FLOAT | No | Yes | No | Configurable |  |  |  | Reports the average flow rate of DIN3, calculated between the prior and current periodic reports.
DIN3 Average Flow Rate | 110 | FLOAT | No | Yes | No | Configurable |  |  |  | Reports the instantaneous flow rate of DIN3, sampled with a 2 second gate time.
DIN3 Config/KFactor | 111 | FLOAT | Yes | No | Yes |  | 0 < |  | 1 | The KFactor to use to calculate DIN3 Flow. This is the number of DIN3 pulses per DIN3 KFactor Unit of volume.
DIN3 Config/KFactor Units | 112 | STRING | Yes | No | Yes |  |  |  | gal | The units of volume of the DIN3 KFactor. (gal, bbl, cm3, L, m3, ft3, Mgal, imp gal, imp Mgal, ML, ac·in, ac·ft)
DIN3 Config/Volume Units | 113 | STRING | Yes | No | Yes |  |  |  | gal | The volume units to use for calculating DIN3 Flow Total. (gal, bbl, cm3, L, m3, ft3, Mgal, imp gal, imp Mgal, ML, ac·in, ac·ft)
DIN3 Config/Timebase | 114 | STRING | Yes | No | Yes |  |  |  | sec | The timebase to use for calculating DIN3 Flow Rates. (sec, min, hour, day)
DIN3 Config/Flowrate Units | 115 | STRING | Yes | No | Yes |  |  |  | gal | The volume units to use for calculating DIN3 Flow Rates. (gal, bbl, cm3, L, m3, ft3, Mgal, imp gal, imp Mgal, ML, ac·in, ac·ft)
AIN2 | 116 | FLOAT | Yes | Yes | No | Configurable |  |  |  | Reports the current reading of the AIN2 terminal, scaled between Scale Low and Scale High. If scaling has not been configured, this will be the same units, range, and value as the "AIN2 Raw" tag. Writing to this tag zeroes AIN2 to the value written.
AIN2 Raw | 117 | FLOAT | No | Yes | No | Configurable |  |  |  | Reports the current reading of the AIN2 terminal. This value is before the scaling, and will be reported as a value in either the 4-20mA, 1-5V, or 0-15V range, depending on the position of the S1 switch on the Ranger's A2D1 Sensor Card.
AIN2 Config/Scale Low | 118 | FLOAT | Yes | No | Yes |  |  |  | 0 | The lower range value to use when scaling AIN2.
AIN2 Config/Scale High | 119 | FLOAT | Yes | No | Yes |  |  |  | 0 | The upper range value to use when scaling AIN2.
AIN2 Config/Scale Adjust | 120 | FLOAT | Yes | No | Yes |  |  |  | 0 | The +/- adjustment to use when scaling AIN2.
AIN2 Config/Scale Units | 121 | STRING | Yes | No | Yes |  |  |  |  | The AIN2 scaled units description.
AIN2 Config/Specific Gravity | 122 | FLOAT | Yes | No | Yes |  |  |  | 1 | The specific gravity to divide the AIN2 reading by, in applications reading liquid level from a pressure sensor.
AIN2 Config/Low Threshold | 123 | FLOAT | Yes | No | Yes | Configurable |  |  | 0 | The low threshold for alarming on AIN2.
AIN2 Config/High Threshold | 124 | FLOAT | Yes | No | Yes | Configurable |  |  | 0 | The high threshold for alarming on AIN2.
AIN2 Config/Zero Offset | 125 | FLOAT | Yes | No | Yes | Configurable |  |  | 0 | The calibrated zero offset for AIN2. Writing 0 to this tag clears the zero offset for AIN2.
AIN2 Flow Total | 126 | FLOAT | Yes | Yes | No | ac·ft |  |  |  | Reports the flow total of AIN2, calculated by scaling AIN2 to ft3/sec and integrating over the time between AIN2 samples. Writing to this tag from SparkPlug will adjust the current flow total to the given value and reset the flow for both this period and last period.
AIN2 Flow This Period | 127 | FLOAT | Yes | Yes | Yes | ac·ft |  |  |  | Reports the flow this period of AIN2, calculated by scaling AIN2 to ft3/sec and integrating over the time between AIN2 samples. Writing 0 to this tag from SparkPlug will reset the value.
AIN2 Flow Last Period | 128 | FLOAT | Yes | Yes | Yes | ac·ft |  |  |  | Reports the flow last period of AIN2, calculated by scaling AIN2 to ft3/sec and integrating over the time between AIN2 samples. Writing 0 to this tag from SparkPlug will reset the value.
AIN2 Config/Volume Units | 129 | STRING | Yes | No | Yes |  |  |  | ac·ft | The volume units to use for calculating AIN2 Flow Total. (ac·ft)
AIN3 | 130 | FLOAT | Yes | Yes | No | Configurable |  |  |  | Reports the current reading of the AIN3 terminal, scaled between Scale Low and Scale High. If scaling has not been configured, this will be the same units, range, and value as the "AIN3 Raw" tag. Writing to this tag zeroes AIN3 to the value written.
AIN3 Raw | 131 | FLOAT | No | Yes | No | Configurable |  |  |  | Reports the current reading of the AIN3 terminal. This value is before the scaling, and will be reported as a value in either the 4-20mA, 1-5V, or 0-15V range, depending on the position of the S2 switch on the Ranger's A2D1 Sensor Card.
AIN3 Config/Scale Low | 132 | FLOAT | Yes | No | Yes |  |  |  | 0 | The lower range value to use when scaling AIN3.
AIN3 Config/Scale High | 133 | FLOAT | Yes | No | Yes |  |  |  | 0 | The upper range value to use when scaling AIN3.
AIN3 Config/Scale Adjust | 134 | FLOAT | Yes | No | Yes |  |  |  | 0 | The +/- adjustment to use when scaling AIN3.
AIN3 Config/Scale Units | 135 | STRING | Yes | No | Yes |  |  |  |  | The AIN3 scaled units description.
AIN3 Config/Specific Gravity | 136 | FLOAT | Yes | No | Yes |  |  |  | 1 | The specific gravity to divide the AIN3 reading by, in applications reading liquid level from a pressure sensor.
AIN3 Config/Low Threshold | 137 | FLOAT | Yes | No | Yes | Configurable |  |  | 0 | The low threshold for alarming on AIN3.
AIN3 Config/High Threshold | 138 | FLOAT | Yes | No | Yes | Configurable |  |  | 0 | The high threshold for alarming on AIN3.
AIN3 Config/Zero Offset | 139 | FLOAT | Yes | No | Yes | Configurable |  |  | 0 | The calibrated zero offset for AIN3. Writing 0 to this tag clears the zero offset for AIN3.
AIN3 Flow Total | 140 | FLOAT | Yes | Yes | No | ac·ft |  |  |  | Reports the flow total of AIN3, calculated by scaling AIN3 to ft3/sec and integrating over the time between AIN3 samples. Writing to this tag from SparkPlug will adjust the current flow total to the given value and reset the flow for both this period and last period.
AIN3 Flow This Period | 141 | FLOAT | Yes | Yes | Yes | ac·ft |  |  |  | Reports the flow this period of AIN3, calculated by scaling AIN3 to ft3/sec and integrating over the time between AIN3 samples. Writing 0 to this tag from SparkPlug will reset the value.
AIN3 Flow Last Period | 142 | FLOAT | Yes | Yes | Yes | ac·ft |  |  |  | Reports the flow last period of AIN3, calculated by scaling AIN3 to ft3/sec and integrating over the time between AIN3 samples. Writing 0 to this tag from SparkPlug will reset the value.
AIN3 Config/Volume Units | 143 | STRING | Yes | No | Yes |  |  |  | ac·ft | The volume units to use for calculating AIN3 Flow Total. (ac·ft)

## properties
SignalFire Ranger Tag Guide: Firmware Revision v0.1.15 - Subject to change in future firmware revisions
Property Name | DataType | Part of periodic report | Rebirth on change | Description
engLow | INT32 or FLOAT | No | Yes | Tag engineering low range value
engHigh | INT32 or FLOAT | No | Yes | Tag engineering high range value
engUnit | STRING | No | Yes | Tag engineering units string